## EIA
Table A-1. Cost and performance characteristics of new central station electricity generating technologies | [10 empty] | Table A-2. Total overnight capital costs of new electricity generating technologies by region
https://www.eia.gov/outlooks/aeo/assumptions/pdf/table_8.2.pdf | [10 empty] | https://www.eia.gov/outlooks/aeo/assumptions/pdf/table_8.2.pdf
Technology |  | First |  | Lead | Base overnight | Technological | Total overnight | Variable | Fixed | Heat | Technology | Total Overnight Cost (2021$/kW)
|  | Available | Size | Time | cost (b) | optimism | cost (d) (e ) | O&M (f) | O&M | rate ((g)
|  | Year (a) | (MW) | (years) | (2021$/kW) | factor (c ) | (2021$/kW) | (2021$/MWh) | (2021$/kW-y) | (Bty/kWh) |  | NYCW | NYUP
Ultra-supercritical coal (USC) |  | 2025 | 650 | 4 | 4074 | 1 | 4074 | 4.71 | 42.49 | 8638 | Ultra-supercritical coal (USC) | NA | 4614
USC with 30% carbon capture and sequestration (CCS) |  | 2025 | 650 | 4 | 5045 | 1.01 | 5096 | 7.41 | 56.84 | 9751 | USC with 30% carbon capture and sequestration (CCS) | NA | 5729
USC with 90% CCS |  | 2025 | 650 | 4 | 6495 | 1.02 | 6625 | 11.49 | 62.34 | 12507 | USC with 90% CCS | NA | 7303
Combined-cycle—single-shaft |  | 2024 | 418 | 3 | 1201 | 1 | 1201 | 2.67 | 14.76 | 6431 | Combined-cycle—single-shaft | 1912 | 1445
Combined-cycle—multi-shaft |  | 2024 | 1083 | 3 | 1062 | 1 | 1062 | 1.96 | 12.77 | 6370 | Combined-cycle—multi-shaft | 1725 | 1238
Combined-cycle with 90% CCS |  | 2024 | 377 | 3 | 2736 | 1.04 | 2845 | 6.11 | 28.89 | 7124 | Combined-cycle with 90% CCS | 3422 | 2953
Internal combustion engine |  | 2023 | 21 | 2 | 2018 | 1 | 2018 | 5.96 | 36.81 | 8295 | Internal combustion engine | 2769 | 2125
Combustion turbine— aeroderivative (h) |  | 2023 | 105 | 2 | 1294 | 1 | 1294 | 4.92 | 17.06 | 9124 | Combustion turbine— aeroderivativeh | 1864 | 1405
Combustion turbine—industrial frame |  | 2023 | 237 | 2 | 785 | 1 | 785 | 4.71 | 7.33 | 9905 | Combustion turbine—industrial frame | 1144 | 854
Fuel cells |  | 2024 | 10 | 3 | 6639 | 1.09 | 7224 | 0.62 | 32.23 | 6469 | Fuel cells | 9201 | 7498
Nuclear—light water reactor |  | 2027 | 2156 | 6 | 6695 | 1.05 | 7030 | 2.48 | 127.35 | 10443 | Nuclear—light water reactor | NA | 7430
Nuclear—small modular reactor |  | 2028 | 600 | 6 | 6861 | 1.1 | 7547 | 3.14 | 99.46 | 10443 | Nuclear—small modular reactor | NA | 8040
Distributed generation—base |  | 2024 | 2 | 3 | 1731 | 1 | 1731 | 9.01 | 20.27 | 8923 | Distributed generation—base | 2754 | 2081
Distributed generation—peak |  | 2023 | 1 | 2 | 2079 | 1 | 2079 | 9.01 | 20.27 | 9907 | Distributed generation—peak | 2994 | 2257
Battery storage |  | 2022 | 50 | 1 | 1316 | 1 | 1316 | 0 | 25.96 | NA | Battery storage | 1351 | 1321 | 1475 | 0.11658
Biomass |  | 2025 | 50 | 4 | 4524 | 1 | 4525 | 5.06 | 131.62 | 13500 | Biomass | 7292 | 5389
Geothermal (i) (j) |  | 2025 | 50 | 4 | 3076 | 1 | 3076 | 1.21 | 143.22 | 8813 | Geothermal (i) (j) | NA | NA
Conventional hydropower (j) |  | 2025 | 100 | 4 | 3083 | 1 | 3083 | 1.46 | 43.78 | NA | Conventional hydropower (j) | NA | 4144
Wind (e ) |  | 2024 | 200 | 3 | 1718 | 1 | 1718 | 0 | 27.57 | NA | Wind (e ) | NA | 2281
Wind offshore (i) |  | 2025 | 400 | 4 | 4833 | 1.25 | 6041 | 0 | 115.16 | NA | Wind offshore (i) | 6079 | 7370
Solar thermal (i) |  | 2024 | 115 | 3 | 7895 | 1 | 7895 | 0 | 89.39 | NA | Solar thermal (i) | NA | NA
Solar photovoltaic (PV) with tracking (e ), (i), (k) |  | 2023 | 150 | 2 | 1327 | 1 | 1327 | 0 | 15.97 | NA | Solar photovoltaic (PV) with tracking (e ), (i), (k) | 1612 | 1357
Solar PV with storage (i),(k) |  | 2023 | 150 | 2 | 1748 | 1 | 1748 | 0 | 33.67 | NA | Solar PV with storage (i),(k) | 2078 | 1796
Notes
(a) | The first year that a new unit could become operational.
(b) | Base cost includes project contingency costs.
(c ) | We apply the technological optimism factor to the first four units of a new, unproven design; it reflects the demonstrated tendency to underestimate actual costs for a first-of-a-kind unit.
(d) | Overnight capital cost includes contingency factors and excludes regional multipliers (except as noted for wind and solar PV) and learning effects. Interest charges are also excluded.
The capital costs represent current costs for plants that would come online in 2022.
(e ) | Total overnight cost for wind and solar PV technologies in the table are the average input value across all 25 electricity market regions, as weighted by the respective
capacity of that type installed during 2020 in each region to account for the substantial regional variation in wind and solar costs (Table 4). The input value used for onshore
wind in AEO2022 was $1,411 per kilowatt (kW), and for solar PV with tracking, it was $1,323/kW, which represents the cost of building a plant excluding regional factors.
Region-specific factors contributing to the substantial regional variation in cost include differences in typical project size across regions, accessibility of resources, and
variation in labor and other construction costs throughout the country.
(f) | O&M = Operations and maintenance.
(g) | The nuclear average heat rate is the weighted average tested heat rate for nuclear units as reported on the Form EIA-860, Annual Electric Generator Report. No heat rate is
reported for battery storage because it is not a primary conversion technology; conversion losses are accounted for when the electricity is first generated; electricity-to
storage losses are accounted for through the additional demand for electricity required to meet load. For hydropower, wind, solar, and geothermal technologies, no heat
rate is reported because the power is generated without fuel combustion, and no set British thermal unit conversion factors exist. The module calculates the average heat
rate for fossil-fuel generation in each year to report primary energy consumption displaced for these resources.
(h) | Combustion turbine aeroderivative units can be built by the module before 2023, if necessary, to meet a region's reserve margin.
(i) | Capital costs are shown before investment tax credits are applied.
(j) | Because geothermal and hydropower cost and performance characteristics are specific for each site, the table entries show the cost of the least expensive plant that could
be built in the Northwest region for hydro and the Great Basin region for geothermal, where most of the proposed sites are located.
(k) | Costs and capacities are expressed in terms of net AC (alternating current) power available to the grid for the installed capacity.

## Compare Costs
Table A-3 Compare IA-Tech-Supplement-Annex-1-Input-Assumptions Spreadsheet to EIA Cost and Performance Characteristics of New Generating Technologies, Annual Energy Outlook 2022 | [10 empty] | Table 1: Caiazza Comment
IA-Tech-Supplement-Annex-1-Input-Assumptions Resource Costs Tables |  |  | EIA Table 1: Cost of new central station electricity generating technologies |  |  |  | EIA Table 2 |  | Percent Difference between IA and EIA |  |  | Percent Difference between IA and EIA
| Resource | Resource | Technology | Base overnight | Technological | Total overnight | Total Overnight Cost (2021$/kW)
Base Capital Costs by Technology (2020 $/kW) | Costs - Mid | Costs - Low |  | cost | optimism | cost |  |  |  |  | Base Capital Costs by Technology (2020 $/kW)
Technology | 2020 | 2020 |  | (2021$/kW) | factor | (2021$/kW) | NYCW | NYUP | NYCW | NYUP | Technology | NYCW | NYUP
Wind | 1411.7596 | 1411.7596 | Wind | 1718 | 1 | 1718 | NA | 2281 |  | 61.57% | Wind |  | 61.57%
Wind - Offshore | 3055 | 3055 | Wind offshore | 4833 | 1.25 | 6041 | 6079 | 7370 | 98.99% | 141.2% | Wind - Offshore | 98.99% | 141.2%
Solar - Tracking | 1183.1202 | 1183.1202 | Solar photovoltaic (PV) with tracking | 1327 | 1 | 1327 | 1612 | 1357 | 36.25% | 14.7% | Solar - Tracking | 36.25% | 14.7%
Solar - Dist Comm | 1948.1079 | 1948.1079 | [8 empty] | Hydro - Large |  | -5.052%
Solar - Dist Res | 3959.0784 | 3959.0784 | [8 empty] | Gas - CCGT | 22.25% | -12.26%
Hydro - Non-Powered Dam | 2828.8365 | 2828.8365 | [8 empty] | Gas - CT - Frame | 77.19% | 33.56%
Hydro - Large | 4364.478 | 4364.478 | Conventional hydropower | 3083 | 1 | 3083 | NA | 4144 |  | -5.052% | Hydrogen - Fuel Cell | 515% | 401.2%
Gas - CCGT | 1411 | 1411 | Combined-cycle—multi-shaft | 1062 | 1 | 1062 | 1725 | 1238 | 22.25% | -12.26% | Battery - Li ion | 495.2% | 481.9%
Gas - CT - Frame | 1052 | 1052 | Combustion turbine— aeroderivative | 1294 | 1 | 1294 | 1864 | 1405 | 77.19% | 33.56%
Hydrogen - Fuel Cell | 1496 | 1496 | Fuel cells | 6639 | 1.09 | 7224 | 9201 | 7498 | 515% | 401.2%
Pumped Storage [Energy, $/kWh] | 135.9456 | 135.9456
Battery - Li [Energy, $/kWh] | 227 | 227 | Battery storage | 1316 | 1 | 1316 | 1351 | 1321 | 495.2% | 481.9%
https://atb.nrel.gov/electricity/2022/utility-scale_battery_storage

## Costs
Capactity Costs | Capacity Analysis | [10 empty] | EIA Costs | Total | 82538.2119 | 373765.7761 | 219943.6142 | 399529.9262 | 396006.3649
| Modeled | Reference 2040 |  | 2040 Scenario 1 |  | 2040 Scenario 2 |  | 2040 Scenario 3 |  | 2040 Scenario 4 |  | Total |  | Scenario Costs ($ million 2021) |  |  |  |  | Scenario Added Capacity (MW)
| 2020 | Total | Added | Total | Added | Total | Added | Total | Added | Total | Added | cost |  | Reference | Scenaro 1 | Scenaro 2 | Scenaro 3 | Scenaro 4 | Reference | Scenaro 1 | Scenaro 2 | Scenaro 3 | Scenaro 4
NYUP Installed Capactity | [11 empty] | (2021$/kW) | [6 empty] | Added | Added | Added | Added | Added
Wind | 1916.9 | 3786.66 | 1869.76 | 6184.88 | 4267.98 | 5845.41 | 3928.51 | 6098.57 | 4181.67 | 6255.18 | 4338.28 | 2281 |  | 4264.9226 | 9735.2624 | 8960.9313 | 9538.3893 | 9895.6167 | 1869.76 | 4267.98 | 3928.51 | 4181.67 | 4338.28
Wind Imports | 0 | 0 | 0 | 6104.31 | 6104.31 | 6396.79 | 6396.79 | 6396.78 | 6396.78 | 6396.79 | 6396.79 | [7 empty] | 0 | 6104.31 | 6396.79 | 6396.78 | 6396.79
Wind_Offshore | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7370 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar | 276.93 | 7079.98 | 6803.05 | 24077.61 | 23800.68 | 27166.19 | 26889.26 | 25154.56 | 24877.63 | 25357.68 | 25080.75 | 1357 |  | 9231.7388 | 32297.5228 | 36488.7258 | 33758.9439 | 34034.5777 | 6803.05 | 23800.68 | 26889.26 | 24877.63 | 25080.75
Distributed Solar | 1462.46 | 5783.44 | 4320.98 | 11205.9 | 9743.44 | 11205.9 | 9743.44 | 11205.89 | 9743.43 | 11205.9 | 9743.44 | 1357 |  | 5863.5699 | 13221.8481 | 13221.8481 | 13221.8345 | 13221.8481 | 4320.98 | 9743.44 | 9743.44 | 9743.43 | 9743.44
Battery Storage | 337.29 | 1612.34 | 1275.05 | 6276.8 | 5939.51 | 6782.68 | 6445.39 | 6703.04 | 6365.75 | 7065.01 | 6727.72 | 1321 |  | 1684.3411 | 7846.0927 | 8514.3602 | 8409.1557 | 8887.3181 | 1275.05 | 5939.51 | 6445.39 | 6365.75 | 6727.72
Pumped Storage | 1435.4 | 1435.4 | 0 | 1435.4 | 0 | 1435.4 | 0 | 1435.4 | 0 | 1435.4 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
Hydro Imports (New) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
Hydro Imports (Existing) | 1485 | 1485 | 0 | 1485 | 0 | 1485 | 0 | 1485 | 0 | 1485 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
In-State Hydro | 4262.2 | 4603.19 | 340.99 | 4606.53 | 344.33 | 4606.53 | 344.33 | 4606.53 | 344.33 | 4606.53 | 344.33 | 4144 |  | 1413.0626 | 1426.9035 | 1426.9035 | 1426.9035 | 1426.9035 | 340.99 | 344.33 | 344.33 | 344.33 | 344.33
Nuclear | 4860.2 | 1287.2 | -3573 | 3355.2 | -1505 | 3355.2 | -1505 | 3355.2 | -1505 | 3355.2 | -1505 | [7 empty] | -3573 | -1505 | -1505 | -1505 | -1505
Gas & FO | 11665.2 | 8460.9 | -3204.3 | 0 | -11665.2 | 0 | -11665.2 | 0 | -11665.2 | 0 | -11665.2 | 1238 | [6 empty] | -3204.3 | -11665.2 | -11665.2 | -11665.2 | -11665.2
Zero-Carbon Firm Resource | 0 | 0 | 0 | 12439.96 | 12439.96 | 11277.73 | 11277.73 | 13589.81 | 13589.81 | 13305.56 | 13305.56 | 7498 |  | 0 | 93274.8201 | 13961.8297 | 101896.3954 | 99765.0889 | 0 | 12439.96 | 11277.73 | 13589.81 | 13305.56 | Scenario 2 burns H2 in a turbine
Hydrogen | 0 | 0 | 0 | 12439.96 | 12439.96 | 11277.73 | 11277.73 | 13589.81 | 13589.81 | 13305.56 | 13305.56 | 1033.5363 |  | 0 | 12857.1502 | 11655.9433 | 14045.5619 | 13751.7792 | 0 | 12439.96 | 11277.73 | 13589.81 | 13305.56
Biomass | 205.6 | 205.6 | 0 | 205.6 | 0 | 205.6 | 0 | 205.6 | 0 | 205.6 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
NYCW Installed Capacity
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.28 | 27.28 | 27.28 | 27.28 | 2281 |  | 0 | 0 | 0 | 62.2257 | 62.2257 | 0 | 0 | 0 | 27.28 | 27.28
Wind Imports | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
Wind_Offshore | 0 | 9000 | 9000 | 14528.63 | 14528.63 | 14363.65 | 14363.65 | 16756.49 | 16756.49 | 15874.67 | 15874.67 | 6079 |  | 54711 | 88319.5418 | 87316.6284 | 101862.7027 | 96502.1189 | 9000 | 14528.63 | 14363.65 | 16756.49 | 15874.67
Solar | 31.5 | 31.5 | 0 | 501.61 | 470.11 | 501.61 | 470.11 | 501.61 | 470.11 | 501.61 | 470.11 | 1612 |  | 0 | 757.8173 | 757.8173 | 757.8173 | 757.8173 | 0 | 470.11 | 470.11 | 470.11 | 470.11
Distributed Solar | 820.95 | 1765.72 | 944.77 | 4558.25 | 3737.3 | 4558.25 | 3737.3 | 4558.25 | 3737.3 | 4558.25 | 3737.3 | 1612 |  | 1522.9692 | 6024.5276 | 6024.5276 | 6024.5276 | 6024.5276 | 944.77 | 3737.3 | 3737.3 | 3737.3 | 3737.3
Battery Storage | 412.71 | 3259.94 | 2847.23 | 3987.56 | 3574.85 | 3930.49 | 3517.78 | 5503.98 | 5091.27 | 4511.18 | 4098.47 | 1351 |  | 3846.6077 | 4829.6224 | 4752.5208 | 6878.3058 | 5537.033 | 2847.23 | 3574.85 | 3517.78 | 5091.27 | 4098.47
Pumped Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
Hydro Imports (New) | 0 | 1250 | 1250 | 2550 | 2550 | 2550 | 2550 | 2550 | 2550 | 2550 | 2550 | [7 empty] | 1250 | 2550 | 2550 | 2550 | 2550
Hydro Imports (Existing) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
In-State Hydro | 6.66 | 6.66 | 0 | 6.66 | 0 | 6.66 | 0 | 6.66 | 0 | 6.66 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
Gas & FO | 14722.9 | 7858.08 | -6864.82 | 0 | -14722.9 | 0 | -14722.9 | 0 | -14722.9 | 0 | -14722.9 | 1725 | [6 empty] | -6864.82 | -14722.9 | -14722.9 | -14722.9 | -14722.9
Zero-Carbon Firm Resource | 0 | 0 | 0 | 10081.03 | 10081.03 | 9737.62 | 9737.62 | 9931.78 | 9931.78 | 10370.72 | 10370.72 | 9201 |  | 0 | 92755.557 | 16797.3945 | 91382.3078 | 95420.9947 | 0 | 10081.03 | 9737.62 | 9931.78 | 10370.72
Hydrogen | 0 | 0 | 0 | 10081.03 | 10081.03 | 9737.62 | 9737.62 | 9931.78 | 9931.78 | 10370.72 | 10370.72 | 1033.5363 |  | 0 | 10419.1104 | 10064.1837 | 10264.8551 | 10718.5155 | 0 | 10081.03 | 9737.62 | 9931.78 | 10370.72
Biomass | 121.4 | 121.4 | 0 | 121.4 | 0 | 121.4 | 0 | 121.4 | 0 | 121.4 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
| Integration Analysis Projections listed in IA-Tech-Supplement-Annex-2-Key-Drivers-Outputs spreadsheet | [17 empty] | 1869.76 | 4267.98 | 3928.51 | 4208.95 | 4365.56
|  | Reference Case |  | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Scenario 4 | [8 empty] | 0 | 6104.31 | 6396.79 | 6396.78 | 6396.79
| 2020 | Total | Added | Total | Added | Total | Added | Total | Added | Total | Added | [7 empty] | 9000 | 14528.63 | 14363.65 | 16756.49 | 15874.67
NYISO_A-E | [18 empty] | 6803.05 | 24270.79 | 27359.37 | 25347.74 | 25550.86
Wind | 1916.9 | 3786.66 | 1869.76 | 4686.37 | 2769.47 | 4346.9 | 2430 | 4600.06 | 2683.16 | 4756.67 | 2839.77 | [7 empty] | 5265.75 | 13480.74 | 13480.74 | 13480.73 | 13480.74
Wind Imports | 0 | 0 | 0 | 6104.31 | 6104.31 | 6396.79 | 6396.79 | 6396.78 | 6396.78 | 6396.79 | 6396.79 | [7 empty] | 4122.28 | 9514.36 | 9963.17 | 11457.02 | 10826.19
Wind_Offshore | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
Solar | 211.97 | 6602.41 | 6390.44 | 18273.79 | 18061.82 | 21362.37 | 21150.4 | 19350.74 | 19138.77 | 19553.86 | 19341.89 | [7 empty] | 1250 | 2550 | 2550 | 2550 | 2550
Dist Solar | 730.33 | 3507.21 | 2776.88 | 6280.84 | 5550.51 | 6280.84 | 5550.51 | 6280.83 | 5550.5 | 6280.84 | 5550.51 | [7 empty] | 0 | 0 | 0 | 0 | 0
Battery Storage | 223.75 | 1083.68 | 859.93 | 5403.1 | 5179.35 | 6086.25 | 5862.5 | 6025.5 | 5801.75 | 5901.46 | 5677.71 | [7 empty] | 340.99 | 344.33 | 344.33 | 344.33 | 344.33
Pumped Storage | 268.3 | 268.3 | 0 | 268.3 | 0 | 268.3 | 0 | 268.3 | 0 | 268.3 | 0 | [7 empty] | -3573 | -1505 | -1505 | -1505 | -1505
Hydro Imports (New) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | -10069.12 | -26388.1 | -26388.1 | -26388.1 | -26388.1
Hydro Imports (Existing) | 1485 | 1485 | 0 | 1485 | 0 | 1485 | 0 | 1485 | 0 | 1485 | 0 | [7 empty] | 0 | 22520.99 | 21015.35 | 23521.59 | 23676.28
In-State Hydro | 3900.8 | 4071.3 | 170.5 | 4071.3 | 170.5 | 4071.3 | 170.5 | 4071.3 | 170.5 | 4071.3 | 170.5 | [7 empty] | 0 | 22520.99 | 21015.35 | 23521.59 | 23676.28
Nuclear | 3355.2 | 1287.2 | -2068 | 3355.2 | 0 | 3355.2 | 0 | 3355.2 | 0 | 3355.2 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
Gas & FO | 4026.1 | 2657.16 | -1368.94 | 0 | -4026.1 | 0 | -4026.1 | 0 | -4026.1 | 0 | -4026.1
Zero-Carbon Firm Resource | 0 | 0 | 0 | 3613.49 | 3613.49 | 3267.59 | 3267.59 | 4356.7 | 4356.7 | 3926.21 | 3926.21
Biomass | 122.7 | 122.7 | 0 | 122.7 | 0 | 122.7 | 0 | 122.7 | 0 | 122.7 | 0
NYISO_F
Wind | 0 | 0 | 0 | 1009.47 | 1009.47 | 1009.47 | 1009.47 | 1009.47 | 1009.47 | 1009.47 | 1009.47
Wind Imports | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind_Offshore | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar | 39.98 | 217.72 | 177.74 | 5245.16 | 5205.18 | 5245.16 | 5205.18 | 5245.16 | 5205.18 | 5245.16 | 5205.18
Dist Solar | 368.76 | 1201.37 | 832.61 | 2154.2 | 1785.44 | 2154.2 | 1785.44 | 2154.2 | 1785.44 | 2154.2 | 1785.44
Battery Storage | 26.25 | 179.47 | 153.22 | 524.53 | 498.28 | 347.24 | 320.99 | 328.36 | 302.11 | 814.38 | 788.13
Pumped Storage | 1167.1 | 1167.1 | 0 | 1167.1 | 0 | 1167.1 | 0 | 1167.1 | 0 | 1167.1 | 0
Hydro Imports (New) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hydro Imports (Existing) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
In-State Hydro | 282.8 | 453.29 | 170.49 | 453.3 | 170.5 | 453.3 | 170.5 | 453.3 | 170.5 | 453.3 | 170.5
Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas & FO | 3014.6 | 3014.59 | -0.01 | 0 | -3014.6 | 0 | -3014.6 | 0 | -3014.6 | 0 | -3014.6
Zero-Carbon Firm Resource | 0 | 0 | 0 | 4294.54 | 4294.54 | 3153.58 | 3153.58 | 4508.21 | 4508.21 | 3902.2 | 3902.2
Biomass | 22.7 | 22.7 | 0 | 22.7 | 0 | 22.7 | 0 | 22.7 | 0 | 22.7 | 0
NYISO_GHI
Wind | 0 | 0 | 0 | 489.04 | 489.04 | 489.04 | 489.04 | 489.04 | 489.04 | 489.04 | 489.04
Wind Imports | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind_Offshore | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar | 24.98 | 259.85 | 234.87 | 558.66 | 533.68 | 558.66 | 533.68 | 558.66 | 533.68 | 558.66 | 533.68
Dist Solar | 363.37 | 1074.86 | 711.49 | 2770.86 | 2407.49 | 2770.86 | 2407.49 | 2770.86 | 2407.49 | 2770.86 | 2407.49
Battery Storage | 87.29 | 349.19 | 261.9 | 349.17 | 261.88 | 349.19 | 261.9 | 349.18 | 261.89 | 349.17 | 261.88
Pumped Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hydro Imports (New) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hydro Imports (Existing) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
In-State Hydro | 78.6 | 78.6 | 0 | 81.93 | 3.33 | 81.93 | 3.33 | 81.93 | 3.33 | 81.93 | 3.33
Nuclear | 1505 | 0 | -1505 | 0 | -1505 | 0 | -1505 | 0 | -1505 | 0 | -1505
Gas & FO | 4624.5 | 2789.15 | -1835.35 | 0 | -4624.5 | 0 | -4624.5 | 0 | -4624.5 | 0 | -4624.5
Zero-Carbon Firm Resource | 0 | 0 | 0 | 4531.93 | 4531.93 | 4856.56 | 4856.56 | 4724.9 | 4724.9 | 5477.15 | 5477.15
Biomass | 60.2 | 60.2 | 0 | 60.2 | 0 | 60.2 | 0 | 60.2 | 0 | 60.2 | 0
NYISO_J
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind Imports | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind_Offshore | 0 | 6000 | 6000 | 9156.41 | 9156.41 | 9268.44 | 9268.44 | 10964.23 | 10964.23 | 10031.96 | 10031.96
Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dist Solar | 235.97 | 649.58 | 413.61 | 1675.63 | 1439.66 | 1675.63 | 1439.66 | 1675.63 | 1439.66 | 1675.63 | 1439.66
Battery Storage | 321.46 | 2426.39 | 2104.93 | 2154.51 | 1833.05 | 2113.6 | 1792.14 | 3189.23 | 2867.77 | 2473.84 | 2152.38
Pumped Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hydro Imports (New) | 0 | 1250 | 1250 | 2550 | 2550 | 2550 | 2550 | 2550 | 2550 | 2550 | 2550
Hydro Imports (Existing) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
In-State Hydro | 3.33 | 3.33 | 0 | 3.33 | 0 | 3.33 | 0 | 3.33 | 0 | 3.33 | 0
Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas & FO | 9608.2 | 4893.91 | -4714.29 | 0 | -9608.2 | 0 | -9608.2 | 0 | -9608.2 | 0 | -9608.2
Zero-Carbon Firm Resource | 0 | 0 | 0 | 6085.81 | 6085.81 | 5821.36 | 5821.36 | 5906.7 | 5906.7 | 6254.85 | 6254.85
Biomass | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NYISO_K
Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.28 | 27.28 | 27.28 | 27.28
Wind Imports | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind_Offshore | 0 | 3000 | 3000 | 5372.22 | 5372.22 | 5095.21 | 5095.21 | 5792.26 | 5792.26 | 5842.71 | 5842.71
Solar | 31.5 | 31.5 | 0 | 501.61 | 470.11 | 501.61 | 470.11 | 501.61 | 470.11 | 501.61 | 470.11
Dist Solar | 584.98 | 1116.14 | 531.16 | 2882.62 | 2297.64 | 2882.62 | 2297.64 | 2882.62 | 2297.64 | 2882.62 | 2297.64
Battery Storage | 91.25 | 833.55 | 742.3 | 1833.05 | 1741.8 | 1816.89 | 1725.64 | 2314.75 | 2223.5 | 2037.34 | 1946.09
Pumped Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hydro Imports (New) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hydro Imports (Existing) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
In-State Hydro | 3.33 | 3.33 | 0 | 3.33 | 0 | 3.33 | 0 | 3.33 | 0 | 3.33 | 0
Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas & FO | 5114.7 | 2964.17 | -2150.53 | 0 | -5114.7 | 0 | -5114.7 | 0 | -5114.7 | 0 | -5114.7
Zero-Carbon Firm Resource | 0 | 0 | 0 | 3995.22 | 3995.22 | 3916.26 | 3916.26 | 4025.08 | 4025.08 | 4115.87 | 4115.87
Biomass | 121.4 | 121.4 | 0 | 121.4 | 0 | 121.4 | 0 | 121.4 | 0 | 121.4 | 0

## Electrolysis Costs
Estimated cost to produce hydrogen needed for DEFR
2020 $/MMBTU
From Integrated Analysis |  |  | Out of state cost of hydrogen | 2020 | 2025 | 2030 | 2035 | 2040 | Notes
2020 $/kW | 1169.2069 |  | Electricity Input Cost | 16.3127 | 16.1978 | 16.0861 | 15.6452 | 15.3336 | Assumes a dedicated solar resource with cap factor of 23.5%
2020 $/MMBTU | 21.1255 |  | Electrolyzer Capital Cost | 22.5027 | 17.7331 | 14.8219 | 11.8267 | 9.5582
MMBTU/kW | 55.3458 |  | Other Capital Costs (Pipeline Blending, Interconnection, etc) | 0.11179 | 0.11155 | 0.11132 | 0.10824 | 0.10656
|  |  | Underground H2 Storage Cost | 1.8922 | 1.8922 | 1.8922 | 1.8922 | 1.8922 | Based on underground salt cavern storage
|  |  | 400-mile Pipeline Cost | 1.3999 | 1.3999 | 1.3999 | 1.3999 | 1.3999 | High pressure pipelines dedicated for H2. Cost estimates come from Argonne National Lab's Hydrogen Delivery Scenario Analysis Model (HDSAM)
|  |  | Variable O&M Cost | 4.3556 | 4.325 | 4.2951 | 4.1774 | 4.0942
|  |  | Total Cost | 46.575 | 41.6596 | 38.6066 | 35.0498 | 32.3847
|  |  | Total Cost $/MW | 515.8662 | 461.4231 | 427.6088 | 388.2135 | 358.6946 | Converted the Integration Analysis cost per mmBtu to MW using the 55.3 conversion factor
|  |  | In-state cost of hydrogen | 2020 | 2025 | 2030 | 2035 | 2040
|  |  | Electricity Input Cost | 0 | 0 | 0 | 0 | 0 | Cost of electricity is captured endogenously in RESOLVE
|  |  | Electrolyzer Capital Cost | 21.1255 | 16.6478 | 13.9148 | 11.1029 | 8.9732 | Electrolyzer CAPEX is consistent with out-of-state. Difference can be attributed to 25% capacity factor assumed
|  |  | Other Capital Costs (Pipeline Blending, Interconnection, etc) | 0.10494 | 0.10472 | 0.10451 | 0.10162 | 0.10004
|  |  | Underground H2 Storage Cost | 1.8922 | 1.8922 | 1.8922 | 1.8922 | 1.8922 | Based on underground salt cavern storage
|  |  | 400-mile Pipeline Cost | 1.3999 | 1.3999 | 1.3999 | 1.3999 | 1.3999 | High pressure pipelines dedicated for H2. Cost estimates come from Argonne National Lab's Hydrogen Delivery Scenario Analysis Model (HDSAM)
|  |  | Variable O&M Cost | 4.3556 | 4.325 | 4.2951 | 4.1774 | 4.0942
|  |  | Subtotal | 28.8783 | 24.3697 | 21.6066 | 18.6742 | 16.4597 | Cost of electricity is captured endogenously in RESOLVE
|  |  | Total Cost $/MW | 319.8568 | 269.9193 | 239.3157 | 206.8358 | 182.3079
2020 $/kW
|  |  | In-state cost of hydrogen ($/kW) | 2020 | 2025 | 2030 | 2035 | 2040
|  |  | Electricity Input Cost | 0 | 0 | 0 | 0 | 0
|  |  | Electrolyzer Capital Cost | 1169.2069 | 921.3848 | 770.1238 | 614.5011 | 496.6308
|  |  | Other Capital Costs (Pipeline Blending, Interconnection, etc) | 5.8082 | 5.7961 | 5.7843 | 5.6242 | 5.5369
|  |  | Underground H2 Storage Cost | 104.7274 | 104.7274 | 104.7274 | 104.7274 | 104.7274
|  |  | 400-mile Pipeline Cost | 77.4806 | 77.4806 | 77.4806 | 77.4806 | 77.4806
|  |  | Variable O&M Cost | 241.0664 | 239.3688 | 237.7183 | 231.203 | 226.5972
|  |  | Subtotal | 1598.2895 | 1348.7576 | 1195.8343 | 1033.5363 | 910.9729
Used 2035 as the cost for building the 2040 electrolyzer costs.
https://seekingalpha.com/article/4392471-hydrogen-vs-natural-gas-for-electric-power-generation
288 | MW | GE 9F.04 gas turbine produces 288 MW of power.
9.3 | million CF | This turbine would use about 9.3 million CF or 22,400 kg of hydrogen per hour.
1104 | MWh | With an 80% efficient electrolysis energy cost of 49.3 kWh/kg, producing that one hour supply of hydrogen would require 1,104 MWh of power for electrolysis.
3.8333 | MWh | With an 80% efficient electrolysis energy cost of 49.3 kWh/kg, producing a one hour supply of hydrogen for one MW of a turbine would require 3.83 MWh of power for electrolysis.
343 | Btu/CF | Higher heating value BTU/CF
3189.9 | mmBtu/hr
11.076 | mmBtu/MW

## NYISO
NYISO Draft Resource Outlook Baseline w/ CLCPA Case Forecast Scenario | [11 empty] | 06 System and Resource Outlook Update
https://www.nyiso.com/documents/20142/30198298/06%20System_Resource_Outlook_CapEx_Updates.pdf/fd3e3ea9-cdb1-c86e-df17-d48f2ed368db | [11 empty] | committees - bic - espwg - meeting-materials - 2022 - 2022-04-26
NYISO Outlook Study Baseline with CLCPA Case Forecast Scenario
[6 empty] | 2040 | Total | Capacity |  | Good Enough (MW)
Installed Capacity (MW) | [5 empty] | Added | cost | Costs |  | 2040 | 2040
Resource | 2019 | 2025 | 2030 | 2035 | 2040 | Capacity | (2021$/kW) | ($ million 2021) |  | Installed | Added
Nuclear | 5400 | 3346 | 3364 | 3364 | 3364 | -2036 |  |  | Nuclear—small modular reactor | 5400 | 5400 | 8040 | 43416
Fossil | 26262 | 21310 | 21232 | 21234 |  | -26262 |  |  | Fossil | 26500 | 20000
DEFR - HcLo |  |  |  |  | 3812 | 3812 |  |  | Combined-cycle—multi-shaft |  | 18500 | 1725 | 31912.5
DEFR - McMo | [5 empty] | 0 |  |  | Combustion turbine—industrial frame |  | 1500 | 1144 | 1716
DEFR- LcHo |  |  | 420 | 7053 | 40938 | 40938
Total DEFR | 0 | 0 | 420 | 7053 | 44750 | 44750 | 7498 | 335535.5
Hydrogen | [5 empty] | 44750 | 1033.5363 | 46250.7492
Hydro | 6331 | 6302 | 7537 | 7540 | 7540 | 1209 | 4144 | 5010.096 | Hydro | 7540 | 1209 | 4144 | 5010.096
LBW | 1985 | 3335 | 9086 | 12612 | 19087 | 17102 | 2281 | 39009.662
OSW |  | 1826 | 5036 | 9000 | 9000 | 9000 | 7370 | 66330
UPV | 32 | 4676 | 4676 | 4676 | 4676 | 4644 | 1357 | 6301.908
BTM-PV | 2116 | 6834 | 10055 | 10828 | 11198 | 9082 | 1357 | 12324.274
Storage | 1405 | 2910 | 4410 | 5793 | 11450 | 10045 | 1321 | 13269.445
Generation (GWh)
Resource | 2019 | 2025 | 2030 | 2035 | 2040 |  |  |  | Existing Dispatchable
Nuclear | 45429 | 28338 | 27444 | 28338 | 27092 |  |  |  | Dispatchable Emissions-Free | 44750 | 28.72%
Fossil | 50520 | 54174 | 19987 | 14516 |  |  |  |  | Battery Storage | 11450 | 7.348%
DEFR - HcLo |  |  |  |  | 33482 |  |  |  | Pumped Storage
DEFR - McMo | [8 empty] | Weather-Dependent | 43961 | 28.21%
DEFR - LcHo |  |  |  |  | 523 |  |  |  | Total | 155815
Hydro | 40034 | 36418 | 46342 | 46392 | 46391
LBW | 4416 | 8189 | 26971 | 38297 | 59362
OSW |  | 7331 | 20186 | 35460 | 35647
UPV | 51 | 8817 | 8816 | 8817 | 8819
BTM-PV | 2761 | 7483 | 11068 | 11983 | 12.454
Storage | 612 | 4347 | 7004 | 10084 | 21339
Total Generation | 146262 | 157088 | 169810 | 195879 | 245109
RE Generation | 47261 | 68238 | 113383 | 140949 | 162672
ZE Generation | 93301 | 100922 | 147831 | 179371 | 245109
Load | 151386 | 152336 | 162122 | 184836 | 221828
Load+Charge | 151773 | 157089 | 169811 | 195879 | 245109
% RE [RE/Load] | 31% | 45% | 70% | 76% | 73%
%ZE[ZE/(Load+Charge)] | 61% | 64% | 87% | 92% | 100%
Emissions (million tons)
| 2019 | 2025 | 2030 | 2035 | 2040
CO2 (million tons) | 22.24 | 23.53 | 8.5 | 6.22 | 0

## Summary
Table 3: Estimated Capacity Additions and Overnight Capital Costs for those Additions | [5 empty] | Table 4 | Table 5
| Integration Analysis Scenario Capacity Added (MW) |  |  |  |  | NYISO Draft Outlook | Caiazza
Resource | Reference | Scenaro 1 | Scenaro 2 | Scenaro 3 | Scenaro 4 | Added MW | Good Enough
Wind | 1869.76 | 4267.98 | 3928.51 | 4208.95 | 4365.56 | 17102
Wind Imports | 0 | 6104.31 | 6396.79 | 6396.78 | 6396.79
Wind_Offshore | 9000 | 14528.63 | 14363.65 | 16756.49 | 15874.67 | 9000
Solar | 6803.05 | 24270.79 | 27359.37 | 25347.74 | 25550.86 | 4644
Distributed Solar | 5265.75 | 13480.74 | 13480.74 | 13480.73 | 13480.74 | 9082
Battery Storage | 4122.28 | 9514.36 | 9963.17 | 11457.02 | 10826.19 | 10045
Pumped Storage | 0 | 0 | 0 | 0 | 0 | 0
Hydro Imports (New) | 1250 | 2550 | 2550 | 2550 | 2550
Hydro Imports (Existing) | 0 | 0 | 0 | 0 | 0
In-State Hydro | 340.99 | 344.33 | 344.33 | 344.33 | 344.33 | 1209 | 1209
Nuclear | -3573 | -1505 | -1505 | -1505 | -1505 |  | 5400
Gas & FO | -10069.12 | -26388.1 | -26388.1 | -26388.1 | -26388.1 |  | 20000
Zero-Carbon Firm Resource | 0 | 22520.99 | 21015.35 | 23521.59 | 23676.28 | 44750
Hydrogen Production | 0 | 22520.99 | 21015.35 | 23521.59 | 23676.28 | 44750
Biomass | 0 | 0 | 0 | 0 | 0
| Integration Analysis Scenario Costs ($ million 2021) |  |  |  |  | NYISO Draft Outlook | Caiazza | Integration Analysis Scenario Costs ($ million 2021)
Resource | Reference | Scenaro 1 | Scenaro 2 | Scenaro 3 | Scenaro 4 | ($ million 2021) | Good Enough | Reference | Scenaro 1 | Scenaro 2 | Scenaro 3 | Scenaro 4
Wind | 4264.9226 | 9735.2624 | 8960.9313 | 9600.6149 | 9957.8424 | 39009.662 | 0
Wind Imports | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0
Wind_Offshore | 54711 | 88319.5418 | 87316.6284 | 101862.7027 | 96502.1189 | 66330 | 0 |  | 33608.5418 | 32605.6284 | 47151.7027 | 41791.1189
Solar | 9231.7388 | 33055.3401 | 37246.5431 | 34516.7612 | 34792.3951 | 6301.908 | 0
Distributed Solar | 7386.5391 | 19246.3757 | 19246.3757 | 19246.3621 | 19246.3757 | 12324.274 | 0 |  | 11859.8366 | 11859.8366 | 11859.823 | 11859.8366
Battery Storage | 5530.9488 | 12675.7151 | 13266.881 | 15287.4615 | 14424.3511 | 13269.445 | 0 |  | 7144.7663 | 7735.9322 | 9756.5127 | 8893.4023
Pumped Storage | 0 | 0 | 0 | 0 | 0
Hydro Imports (New) | 0 | 0 | 0 | 0 | 0
Hydro Imports (Existing) | 0 | 0 | 0 | 0 | 0
In-State Hydro | 1413.0626 | 1426.9035 | 1426.9035 | 1426.9035 | 1426.9035 | 5010.096 | 5010.096
Nuclear | 0 | 0 | 0 | 0 | 0 |  | 43416
Gas & FO | 0 | 0 | 0 | 0 | 0 |  | 33628.5
Zero-Carbon Firm Resource | 0 | 186030.3771 | 30759.2242 | 193278.7032 | 195186.0836 | 335535.5 | 0
Hydrogen Production | 0 | 23276.2605 | 21720.127 | 24310.417 | 24470.2947 | 46250.7492 | 0
Biomass | 0 | 0 | 0 | 0 | 0
Total | 82538.2119 | 373765.7761 | 219943.6142 | 399529.9262 | 396006.3649 | 524031.6342 | 82054.596 |  | 52613.1446 | 52201.3971 | 68768.0385 | 62544.3578 | 61171.2645
Cost for Additional Capacity Installed for replacement at expected lifetime | [9 empty] | 52.2014 | 68.768 | 62.5444
Total | 82538.2119 |  | 219943.6142 | 399529.9262 | 396006.3649
2040 | 8706.8048 |  | 27927.9077 | 25698.1668 | 24323.595
2050 | 72268.3776 |  | 278561.0097 | 304427.5424 | 246152.3252
2040 | 10.55% |  | 12.7% | 6.432% | 6.142%
2050 | 87.56% |  | 126.7% | 76.2% | 62.16%
0.31162

## Sheet5 (hidden)
Fossil Additions per Gold Book
3091
2011 | 549
2012 | 494
2013
2014 | 167
2015
2016
2017 | 104
2018 | 744
2019 | 1020
2020
2021 | 13

## Retirement
Cost for Additional Capacity Installed for replacement at expected lifetime
| Replacement Capacity (MW) |  |  |  |  | Total Cost | Replacement Cost
Scenario 2 | 2025 | 2030 | 2035 | 2040 | Total | (2021$/kW) | ($ million)
Zero-Carbon Firm Resource | 0 | 0 | 0 | 0 | 0 | 8531.5363 | 0 | 21015.35 | 179293.2213
Wind |  |  |  | 1916.9 | 1916.9 | 2281 | 4372.4489 | 3814.08 | 8699.9165
Wind_Offshore |  |  |  | 0 | 0 | 7370 | 0 | 6200 | 45694
Solar |  |  |  | 14438.01 | 14438.01 | 1357 | 19592.3796 | 22639.48 | 30721.7744
Battery Storage |  | 750 | 750.01 | 1500.05 | 3000.06 | 1321 | 3963.0793 | 10713.17 | 14152.0976
[6 empty] | Total | 27927.9077 |  | 278561.0097
| Replacement Capacity (MW) |  |  |  |  | Total Cost | Replacement Cost
Scenario 3 | 2025 | 2030 | 2035 | 2040 | Total | (2021$/kW) | ($ million)
Zero-Carbon Firm Resource | 0 | 0 | 0 | 0 | 0 | 8531.5363 | 0 | 23521.59 | 200675.2988
Wind |  |  |  | 1916.9 | 1916.9 | 2281 | 4372.4489 | 4600.06 | 10492.7369
Wind_Offshore |  |  |  | 0 | 0 | 7370 | 0 | 6600 | 48642
Solar |  |  |  | 12794.87 | 12794.87 | 1357 | 17362.6386 | 20996.34 | 28492.0334
Battery Storage |  | 750.02 | 750 | 1500.04 | 3000.06 | 1321 | 3963.0793 | 12207.02 | 16125.4734
[6 empty] | Total | 25698.1668 |  | 304427.5424
| Replacement Capacity (MW) |  |  |  |  | Total Cost | Replacement Cost
Scenario 4 | 2025 | 2030 | 2035 | 2040 | Total | (2021$/kW) | ($ million)
Zero-Carbon Firm Resource | 0 | 0 | 0 | 0 | 0 | 8531.5363 | 0 | 23676.28 | 201995.0421
Wind |  |  |  | 1916.9 | 1916.9 | 2281 | 4372.4489 | 3859.26 | 8802.9721
Wind_Offshore |  |  |  | 0 | 0 | 7370 | 0 |  | 0
Solar |  |  |  | 11781.96 | 11781.96 | 1357 | 15988.1197 | 6600 | 8956.2
Battery Storage |  | 750 | 750 | 1500.02 | 3000.02 | 1321 | 3963.0264 | 19983.43 | 26398.111
[6 empty] | Total | 24323.595 | 11576.19 | 246152.3252
| Replacement Capacity (MW) |  |  |  |  | Total Cost | Replacement Cost
Reference Case | 2025 | 2030 | 2035 | 2040 | Total | (2021$/kW) | ($ million)
Zero-Carbon Firm Resource | 0 | 0 | 0 | 0 | 0 | 8531.5363 | 0 |  | 0
Wind |  |  |  | 1916.9 | 1916.9 | 2281 | 4372.4489 | 3786.66 | 8637.3715
Wind_Offshore |  |  |  | 0 | 0 | 7370 | 0 | 6200 | 45694
Solar |  |  |  | 273.64 | 273.64 | 1357 | 371.3295 | 8475.11 | 11500.7243
Battery Storage |  | 750 | 750.03 | 1499.99 | 3000.02 | 1321 | 3963.0264 | 4872.28 | 6436.2819
[6 empty] | Total | 8706.8048 |  | 72268.3776
Additional Capacity Installed for replacement at expected lifetime
Scenario 2 | 2025 | 2030 | 2035 | 2040 | Total
Wind |  |  |  | 1916.9 | 3814.08
Wind_Offshore |  |  |  | 0 | 6200
Solar |  |  |  | 14438.01 | 22639.48
Battery Storage |  | 750 | 750.01 | 1500.05 | 10713.17
Scenario 3 | 2025 | 2030 | 2035 | 2040 | Total
Wind |  |  |  | 1916.9 | 4600.06
Wind_Offshore |  |  |  | 0 | 6600
Solar |  |  |  | 12794.87 | 20996.34
Battery Storage |  | 750.02 | 750 | 1500.04 | 12207.02
Scenario 4 | 2025 | 2030 | 2035 | 2040 | Total
Wind |  |  |  | 1916.9 | 3859.26
Wind_Offshore |  |  |  | 0 | 6600
Solar |  |  |  | 11781.96 | 19983.43
Battery Storage |  | 750 | 750 | 1500.02 | 11576.19
Reference Case | 2025 | 2030 | 2035 | 2040 | Total
Wind |  |  |  | 1916.9 | 3786.66
Wind_Offshore |  |  |  | 0 | 6200
Solar |  |  |  | 273.64 | 8475.11
Battery Storage |  | 750 | 750.03 | 1499.99 | 4872.28